## Sheet1
ErrorIndex | SimulationIndex | ErrorType | ErrorMessage | Count
1 | 1 | 0 | GetHTSurfaceData: Surfaces with interface to Ground found but no "Ground Temperatures" were input. Found first in surface=SPACE 1-3:SLAB 1.1 Defaults, constant throughout the year of (18.0) will be used. | 1
2 | 1 | 0 | CheckConvexity: Zone="THERMAL ZONE 1-1", Surface="SPACE 2-1:SLAB 3.2" is non-convex. ...vertex 2 to vertex 3 to vertex 4 ...vertex 2=[97.18,32.00,7.21] ...vertex 3=[88.18,32.00,7.21] ...vertex 4=[88.18,39.26,7.21] | 1
3 | 1 | 0 | CheckConvexity: Zone="THERMAL ZONE 3-1", Surface="SPACE 3-1:SLAB 4.1" is non-convex. ...vertex 2 to vertex 3 to vertex 4 ...vertex 2=[101.14,43.33,8.43] ...vertex 3=[99.62,43.33,8.43] ...vertex 4=[99.62,49.13,8.43] | 1
4 | 1 | 0 | GetSurfaceData: Construction ARCHERY INTERIOR M27Q25 WALL C of interzone surface SPACE 1-3:WALL-1.78:SPACE 1-2 does not have the same materials in the reverse order as the construction ARCHERY INTERIOR M27Q25 WALL C of adjacent surface SPACE 1-2:WALL-1.78:SPACE 1-3 ...but Nominal U values are similar, diff=[0.0000] ... simulation proceeds. ...if the two zones are expected to have significantly different temperatures, the proper "reverse" construction should be created. ...this problem for this pair will not be reported again. | 1
5 | 1 | 0 | GetSurfaceData: Construction ARCHERY INTERIOR NO PCM WALL G RANGE of interzone surface SPACE 1-7:WALL 1.17:SPACE 1-1 does not have the same materials in the reverse order as the construction ARCHERY INTERIOR NO PCM WALL G RANGE of adjacent surface SPACE 1-1:WALL 1.17:SPACE 1-7 ...but Nominal U values are similar, diff=[0.0000] ... simulation proceeds. ...this problem for this pair will not be reported again. | 1
6 | 1 | 0 | GetSurfaceData: Construction ARCHERY INTERIOR M27Q23 WALL B of interzone surface SPACE 2-2:WALL 2.28:SPACE 2-3 does not have the same materials in the reverse order as the construction ARCHERY INTERIOR M27Q23 WALL B of adjacent surface SPACE 2-3:WALL 2.28:SPACE 2-2 ...but Nominal U values are similar, diff=[0.0000] ... simulation proceeds. ...this problem for this pair will not be reported again. | 1
7 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.23:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 CDF1B, Zone=THERMAL ZONE 1-6 | 1
8 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 E1288, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 D80EC, Zone=THERMAL ZONE 1-6 | 1
9 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 D80EC, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 E1288, Zone=THERMAL ZONE 1-6 | 1
10 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.23:SPACE 1-6 CDF1B, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.23:SPACE 1-6, Zone=THERMAL ZONE 1-6 | 1
11 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.24:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.24:SPACE 1-6 A7888, Zone=THERMAL ZONE 1-6 | 1
12 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.27:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.27:SPACE 1-6 E2A69, Zone=THERMAL ZONE 1-6 | 1
13 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.27:SPACE 1-6 E2A69, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.27:SPACE 1-6, Zone=THERMAL ZONE 1-6 | 1
14 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.50:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.50:SPACE 1-6 53CC0, Zone=THERMAL ZONE 1-6 | 1
15 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.50:SPACE 1-6 53CC0, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.50:SPACE 1-6, Zone=THERMAL ZONE 1-6 | 1
16 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.51:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 769CE, Zone=THERMAL ZONE 1-6 | 1
17 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 B2DCD, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 554A2, Zone=THERMAL ZONE 1-6 | 1
18 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 554A2, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 B2DCD, Zone=THERMAL ZONE 1-6 | 1
19 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.51:SPACE 1-6 769CE, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.51:SPACE 1-6, Zone=THERMAL ZONE 1-6 | 1
20 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-6:WALL 1.52:SPACE 1-6, Zone=THERMAL ZONE 1-6 Surface=SPACE 1-6:WALL 1.52:SPACE 1-6 02E5D, Zone=THERMAL ZONE 1-6 | 1
21 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-9:WALL 1.50:SPACE 1-9, Zone=THERMAL ZONE 1-9 Surface=SPACE 1-9:WALL 1.50:SPACE 1-9 67099, Zone=THERMAL ZONE 1-9 | 1
22 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-9:WALL 1.50:SPACE 1-9 67099, Zone=THERMAL ZONE 1-9 Surface=SPACE 1-9:WALL 1.50:SPACE 1-9, Zone=THERMAL ZONE 1-9 | 1
23 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-10:WALL 1.59:SPACE 1-10, Zone=THERMAL ZONE 1-10 Surface=SPACE 1-10:WALL 1.59:SPACE 1-10 87919, Zone=THERMAL ZONE 1-10 | 1
24 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-11:WALL 1.47:SPACE 1-11, Zone=THERMAL ZONE 1-11 Surface=SPACE 1-11:WALL 1.47:SPACE 1-11 747C1, Zone=THERMAL ZONE 1-11 | 1
25 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-8:WALL 1.27:SPACE 1-8, Zone=THERMAL ZONE 1-8 Surface=SPACE 1-8:WALL 1.27:SPACE 1-8 3CBD4, Zone=THERMAL ZONE 1-8 | 1
26 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-8:WALL 1.27:SPACE 1-8 3CBD4, Zone=THERMAL ZONE 1-8 Surface=SPACE 1-8:WALL 1.27:SPACE 1-8, Zone=THERMAL ZONE 1-8 | 1
27 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL 1.62:SPACE 1-26, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL 1.62:SPACE 1-26 0A49E, Zone=THERMAL ZONE 1-26 | 1
28 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL 1.62:SPACE 1-26 0A49E, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL 1.62:SPACE 1-26, Zone=THERMAL ZONE 1-26 | 1
29 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL-1.75:SPACE 1-26, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL-1.75:SPACE 1-26 728E2, Zone=THERMAL ZONE 1-26 | 1
30 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL-1.75:SPACE 1-26 728E2, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL-1.75:SPACE 1-26, Zone=THERMAL ZONE 1-26 | 1
31 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL-1.74:SPACE 1-26, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL-1.74:SPACE 1-26 F5662, Zone=THERMAL ZONE 1-26 | 1
32 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 1-26:WALL-1.74:SPACE 1-26 F5662, Zone=THERMAL ZONE 1-26 Surface=SPACE 1-26:WALL-1.74:SPACE 1-26, Zone=THERMAL ZONE 1-26 | 1
33 | 1 | 0 | GetSurfaceData: Construction ARCHERY INTERIOR M51Q25 WALL D of interzone surface SPACE 2-24:WALL 2.53:SPACE 2-10 does not have the same materials in the reverse order as the construction ARCHERY INTERIOR M51Q25 WALL D of adjacent surface SPACE 2-10:WALL 2.53:SPACE 2-24 ...but Nominal U values are similar, diff=[0.0000] ... simulation proceeds. ...this problem for this pair will not be reported again. | 1
34 | 1 | 0 | GetSurfaceData: CAUTION -- Interzone surfaces are usually in different zones Surface=SPACE 2-24:WALL 2.57:SPACE 2-24, Zone=THERMAL ZONE 2-24 Surface=SPACE 2-24:WALL 2.57:SPACE 2-24 44E5F, Zone=THERMAL ZONE 2-24 | 1
35 | 1 | 0 | DetermineShadowingCombinations: Surface="SPACE 2-1:SLAB 3.2" is a receiving surface and is non-convex. ...Shadowing values may be inaccurate. Check .shd report file for more surface shading details | 1
36 | 1 | 0 | DetermineShadowingCombinations: Surface="SPACE 3-1:SLAB 4.1" is a receiving surface and is non-convex. ...Shadowing values may be inaccurate. Check .shd report file for more surface shading details | 1
37 | 1 | 0 | Calculated design heating load for zone=THERMAL ZONE 2-18 is zero. Check Sizing:Zone and ZoneControl:Thermostat inputs. | 1
38 | 1 | 0 | ManageSizing: For a plant sizing run, there must be at least 1 Sizing:Plant object input. SimulationControl Plant Sizing option ignored. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 8.73425E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 8.73425E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.65255E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.65255E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
39 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 1-3¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 8.734253E-002 ...Requested capacity ( W ) = 1426.264 ...Requested flow/capacity ratio ( m3/s/W ) = 6.123E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 1445.829 | 1
40 | 1 | 0 | SizeDXCoil Coil:Heating:DX:VariableRefrigerantFlow THERMAL ZONE 1-3¦VTU-1¦VRF HEATING COIL ...Gross Rated Heating Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 8.734253E-002 ...Requested capacity ( W ) = 1445.829 ...Requested flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 1445.829 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.10877 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.10877 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 9.64812E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 9.64812E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.32151 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.32151 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.11509 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.15526 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.11509 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 4.99601E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 4.99601E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.19496E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.19496E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.15147 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.15147 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 2.93118E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 2.93118E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
41 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 1-6¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.151470 ...Requested capacity ( W ) = 2465.379 ...Requested flow/capacity ratio ( m3/s/W ) = 6.143E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 2507.376 | 1
42 | 1 | 0 | SizeDXCoil Coil:Heating:DX:VariableRefrigerantFlow THERMAL ZONE 1-6¦VTU-1¦VRF HEATING COIL ...Gross Rated Heating Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.151470 ...Requested capacity ( W ) = 2507.376 ...Requested flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 2507.376 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 2.26393E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 2.26393E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 7.13188E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 7.13188E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.57468E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.57468E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 4.71826E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 4.71826E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.77304E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.77304E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 5.95397E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 5.95397E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 6.85841E-003 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 6.85841E-003 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.66206E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.66206E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.98015E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.98015E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 5.62605E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 5.62605E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 4.69275E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 4.69275E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 3.77537E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 4.24178E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 3.77537E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 4.24178E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
43 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 1-12¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the minimum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate (m3/s ) = 4.692747E-002 ...Requested capacity (W ) = 1174.629 ...Requested flow/capacity ratio (m3/s/W ) = 3.995E-005 ...Minimum flow/capacity ratio (m3/s/W ) = 4.027E-005 ...Adjusted capacity ( W ) = 1165.320 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 7.94625E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 7.94625E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 6.71601E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 6.71601E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.42258 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.42258 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.10631 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.10631 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 2.23011E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 2.23011E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.08759E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.08759E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 2.81457E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74375 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 2.81457E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.22493E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.21850 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.22493E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.14158 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 7.05148E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.14158 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 7.05148E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 1.98207E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 2.42128E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 1.98207E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 2.42128E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.14158 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 2.50880E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.14158 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 2.50880E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 1.98207E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 8.03240E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 1.98207E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 8.03240E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.18405 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.98929 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.18405 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.98929 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 4.86078E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.15260 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 4.86078E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.15260 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
44 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 1-26¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.989289 ...Requested capacity ( W ) = 15014.239 ...Requested flow/capacity ratio ( m3/s/W ) = 6.589E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 16376.250 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.14488 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 5.02554E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.14488 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 5.02554E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.10819 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.10819 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
45 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 1-18¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.108193 ...Requested capacity ( W ) = 1737.964 ...Requested flow/capacity ratio ( m3/s/W ) = 6.225E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 1790.990 User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.37754 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74379 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74379 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.37756 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.37756 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.74379 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.74379 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.74656 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.37756 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.37756 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.70915 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.33318 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.20470 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.33318 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.20470 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 8.40019E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 9.70079E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 8.40019E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 9.70079E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.12337 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.12337 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 6.98443E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 6.94866E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 6.98443E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 6.94866E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
46 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-5¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.123373 ...Requested capacity ( W ) = 1722.220 ...Requested flow/capacity ratio ( m3/s/W ) = 7.163E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 2042.275 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.24160 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.24160 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.81415E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.81415E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 9.10807E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.72201E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 9.10807E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.72201E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.30043 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.63332 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.30043 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.33129 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 4.05933E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.33129 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 4.05933E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
47 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-8¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.300433 ...Requested capacity ( W ) = 4587.984 ...Requested flow/capacity ratio ( m3/s/W ) = 6.548E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 4973.240 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.20057 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 9.96657E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.20057 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 9.96657E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
48 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-18¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 9.966573E-002 ...Requested capacity ( W ) = 1309.848 ...Requested flow/capacity ratio ( m3/s/W ) = 7.608E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 1649.821 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.18405 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.13066 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.18405 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.13066 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 3.53941E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.49918E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 3.53941E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.49918E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
49 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-9¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.130663 ...Requested capacity ( W ) = 1954.580 ...Requested flow/capacity ratio ( m3/s/W ) = 6.684E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 2162.943 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.10606 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.10606 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 2.01205E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.15479 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 2.01205E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 2.07645E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 6.85910E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 2.07645E-002 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 6.85910E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.76536E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.76536E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.87437E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.87437E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.35795E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.35795E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.79761E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.79761E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 4.83193E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 4.83193E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 2.64258E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 2.64258E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 4.41715E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 4.41715E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 2.40852E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 2.40852E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.07791E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.07791E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.58921E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.58921E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 3.02444E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 3.02444E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 1.58921E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 1.58921E-002 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.09961E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.09961E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 4.72010E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 4.72010E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.19962E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.19962 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.19962E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 3.86810E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.35394 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 3.86810E-003 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.14488 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 0.12582 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.14488 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 0.12582 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
50 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-13¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 0.125823 ...Requested capacity ( W ) = 1940.830 ...Requested flow/capacity ratio ( m3/s/W ) = 6.482E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 2082.829 User-Specified Cooling Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 5.68316E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 0.16517 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 5.68316E-002 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Cooling Supply Air Flow Rate [m3/s] = 1.39972 differs from Design Size Cooling Supply Air Flow Rate [m3/s] = 1.20284 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Heating Supply Air Flow Rate [m3/s] = 1.39972 differs from Design Size Heating Supply Air Flow Rate [m3/s] = 1.20284 This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Cooling Operation of 0.14488 [m3/s] differs from Design Size Outdoor Air Flow Rate During Cooling Operation of 0.20804 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. User-Specified Outdoor Air Flow Rate During Heating Operation of 0.14488 [m3/s] differs from Design Size Outdoor Air Flow Rate During Heating Operation of 0.20804 [m3/s] This may, or may not, indicate mismatched component sizes. Verify that the value entered is intended and is consistent with other components. | 1
51 | 1 | 0 | SizeDXCoil Coil:Cooling:DX:VariableRefrigerantFlow THERMAL ZONE 2-24¦VTU-1¦VRF COOLING COIL ...Gross Rated Total Cooling Capacity [W] will be limited by the maximum rated volume flow per rated total capacity ratio. ...DX coil volume flow rate ( m3/s ) = 1.202841 ...Requested capacity ( W ) = 18758.006 ...Requested flow/capacity ratio ( m3/s/W ) = 6.412E-005 ...Maximum flow/capacity ratio ( m3/s/W ) = 6.041E-005 ...Adjusted capacity ( W ) = 19911.303 | 1
52 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-3¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 8.7343E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
53 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-3¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.1553 m3/s ... Supply Air Flow Rate During Cooling Operation = 8.7343E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
54 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-3¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 8.7343E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
55 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-3¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.1553 m3/s ... Supply Air Flow Rate During Heating Operation = 8.7343E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
56 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-7¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.1088 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
57 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-7¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.1553 m3/s ... Supply Air Flow Rate During Cooling Operation = 0.1088 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
58 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-7¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.1088 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
59 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-7¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.1553 m3/s ... Supply Air Flow Rate During Heating Operation = 0.1088 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
60 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-2¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.3215 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
61 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-2¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.3215 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
62 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-4¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 4.9960E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
63 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-4¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 4.9960E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
64 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-4¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 4.9960E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
65 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-4¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 4.9960E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
66 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-6¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 0.1515 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
67 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-6¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 0.1515 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
68 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-6¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 0.1515 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
69 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-6¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 0.1515 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
70 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-9¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.2639E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
71 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-9¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 2.2639E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
72 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-9¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.2639E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
73 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-9¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 2.2639E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
74 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-10¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.5747E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
75 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-10¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 1.5747E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
76 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-10¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.5747E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
77 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-10¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 1.5747E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
78 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-11¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.7730E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
79 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-11¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 1.7730E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
80 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-11¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.7730E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
81 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-11¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 1.7730E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
82 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-20¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 6.8584E-003 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
83 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-20¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 6.8584E-003 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
84 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-20¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 6.8584E-003 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
85 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-20¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 6.8584E-003 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
86 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-8¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.9802E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
87 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-8¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 1.9802E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
88 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-8¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 1.9802E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
89 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-8¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 1.9802E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
90 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-12¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 4.6927E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
91 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-12¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 4.6927E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
92 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-13¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 7.9462E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
93 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-13¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 7.9462E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
94 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-13¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 7.9462E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
95 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-13¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 7.9462E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
96 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-14¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 0.4226 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
97 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-14¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 0.4226 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
98 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-21¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.2301E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
99 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-21¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 2.2301E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
100 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-21¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.2301E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
101 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-21¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 2.2301E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
102 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-22¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.8146E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
103 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-22¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.2185 m3/s ... Supply Air Flow Rate During Cooling Operation = 2.8146E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
104 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-22¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.7437 m3/s ... Max Fan Volume Flow Rate = 2.8146E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
105 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-22¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.2185 m3/s ... Supply Air Flow Rate During Heating Operation = 2.8146E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
106 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-15¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1416 m3/s ... Max Fan Volume Flow Rate = 7.0515E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
107 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-15¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1416 m3/s ... Max Fan Volume Flow Rate = 7.0515E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
108 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-23¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1416 m3/s ... Max Fan Volume Flow Rate = 2.5088E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
109 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-23¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1416 m3/s ... Max Fan Volume Flow Rate = 2.5088E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
110 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-17¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1449 m3/s ... Max Fan Volume Flow Rate = 5.0255E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
111 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-17¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1449 m3/s ... Max Fan Volume Flow Rate = 5.0255E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
112 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-18¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 0.1082 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
113 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 1-18¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 0.1082 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
114 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-3¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.3332 m3/s ... Max Fan Volume Flow Rate = 0.2047 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
115 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-3¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.3332 m3/s ... Max Fan Volume Flow Rate = 0.2047 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
116 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-5¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 0.1234 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
117 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-5¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 0.1234 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
118 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-6¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.2416 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
119 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-6¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.2416 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
120 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-7¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 3.8141E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
121 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-7¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 9.1081E-002 m3/s ... Supply Air Flow Rate During Cooling Operation = 3.8141E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
122 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-7¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 3.8141E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
123 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-7¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 9.1081E-002 m3/s ... Supply Air Flow Rate During Heating Operation = 3.8141E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
124 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-8¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.3004 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
125 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-8¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3313 m3/s ... Supply Air Flow Rate During Cooling Operation = 0.3004 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
126 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-8¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.6333 m3/s ... Max Fan Volume Flow Rate = 0.3004 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
127 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-8¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3313 m3/s ... Supply Air Flow Rate During Heating Operation = 0.3004 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
128 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-18¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.2006 m3/s ... Max Fan Volume Flow Rate = 9.9666E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
129 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-18¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.2006 m3/s ... Max Fan Volume Flow Rate = 9.9666E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
130 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-9¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1840 m3/s ... Max Fan Volume Flow Rate = 0.1307 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
131 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-9¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1840 m3/s ... Max Fan Volume Flow Rate = 0.1307 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
132 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-11¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 0.1061 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
133 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-11¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 0.1061 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
134 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-12¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 2.0121E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
135 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-12¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 2.0765E-002 m3/s ... Supply Air Flow Rate During Cooling Operation = 2.0121E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
136 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-12¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1548 m3/s ... Max Fan Volume Flow Rate = 2.0121E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
137 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-12¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 2.0765E-002 m3/s ... Supply Air Flow Rate During Heating Operation = 2.0121E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
138 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-14¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.7654E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
139 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-14¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 3.7654E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
140 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-14¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.7654E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
141 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-14¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 3.7654E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
142 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-15¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.3580E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
143 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-15¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 3.3580E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
144 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-15¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.3580E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
145 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-15¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 3.3580E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
146 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-16¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 4.8319E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
147 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-16¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 4.8319E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
148 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-16¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 4.8319E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
149 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-16¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 4.8319E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
150 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-17¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 4.4172E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
151 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-17¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 4.4172E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
152 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-17¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 4.4172E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
153 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-17¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 4.4172E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
154 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-20¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.0779E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
155 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-20¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 3.0779E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
156 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-20¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.0779E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
157 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-20¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 3.0779E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
158 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-21¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.0244E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
159 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-21¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 3.0244E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
160 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-21¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 3.0244E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
161 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-21¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 3.0244E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
162 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-22¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 1.0996E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
163 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-22¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 1.0996E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
164 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-22¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 1.0996E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
165 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-22¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 1.0996E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
166 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-23¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 1.1996E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
167 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-23¦VTU-1"] ...The Outdoor Air Flow Rate During Cooling Operation exceeds the Supply Air Flow Rate During Cooling Operation. ...Outdoor Air Flow Rate During Cooling Operation = 0.3539 m3/s ... Supply Air Flow Rate During Cooling Operation = 1.1996E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
168 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-23¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.1996 m3/s ... Max Fan Volume Flow Rate = 1.1996E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
169 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-23¦VTU-1"] ...The Outdoor Air Flow Rate During Heating Operation exceeds the Supply Air Flow Rate During Heating Operation. ...Outdoor Air Flow Rate During Heating Operation = 0.3539 m3/s ... Supply Air Flow Rate During Heating Operation = 1.1996E-002 m3/s ...the outdoor air flow rate will be reduced to match and the simulation continues. | 1
170 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-13¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1449 m3/s ... Max Fan Volume Flow Rate = 0.1258 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
171 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-13¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1449 m3/s ... Max Fan Volume Flow Rate = 0.1258 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
172 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-25¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 5.6832E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
173 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-25¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 0.1652 m3/s ... Max Fan Volume Flow Rate = 5.6832E-002 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
174 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-24¦VTU-1"] ... has Supply Air Flow Rate During Cooling Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Cooling Operation = 1.3997 m3/s ... Max Fan Volume Flow Rate = 1.2028 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
175 | 1 | 0 | InitVRF: VRF Terminal Unit = [ZoneHVAC:TerminalUnit:VariableRefrigerantFlow, "THERMAL ZONE 2-24¦VTU-1"] ... has Supply Air Flow Rate During Heating Operation > Max Fan Volume Flow Rate, should be <= ... Supply Air Flow Rate During Heating Operation = 1.3997 m3/s ... Max Fan Volume Flow Rate = 1.2028 m3/s ...the supply air flow rate during cooling operation will be reduced to match and the simulation continues. | 1
176 | 1 | 0 | GetNextEnvironment: Adaptive Comfort being reported during design day. | 1
177 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.101E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 07:00 - 07:10 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
178 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.738E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 14:10 - 14:20 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
179 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.730E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 07:00 - 07:01 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
180 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.730E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 07:00 - 07:01 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
181 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.058E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 07:00 - 07:01 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
182 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range at 1.058E-005 m3/s/W. During Warmup, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 07:00 - 07:01 Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--8.056E-005] Possible causes include inconsistent air flow rates in system components or inconsistent supply air fan operation modes in coil and unitary system objects. | 0
183 | 1 | 0 | Temperature out of range [-100. to 200.] (PsyPsatFnTemp) Routine=CalcDXHeatingCoil:fullload, Environment=SAN-DIEGO-GILLESPIE ANN HTG 99.6% CONDNS DB, at Simulation time=01/21 00:01 - 00:02 Input Temperature=598.80 | 0
184 | 1 | 0 | UtilityCost: Spaces were removed from the variable="FLATENERGYCHARGE-ELECTRICITY 0.05". ...Resultant variable="FLATENERGYCHARGE-ELECTRICITY0.05". | 1
185 | 1 | 0 | UtilityCost: Spaces were removed from the variable="COST 0.05 CURRENCY". ...Resultant variable="COST0.05CURRENCY". | 1
186 | 1 | 0 | UtilityCost: Spaces were removed from the variable="FLATENERGYCHARGE-GAS 0.5". ...Resultant variable="FLATENERGYCHARGE-GAS0.5". | 1
187 | 1 | 0 | UtilityCost: Spaces were removed from the variable="COST 0.5 CURRENCY". ...Resultant variable="COST0.5CURRENCY". | 1
188 | 1 | 0 | UtilityCost: Spaces were removed from the variable="COST 0.05 CURRENCY". ...Resultant variable="COST0.05CURRENCY". | 1
189 | 1 | 0 | UtilityCost: Spaces were removed from the variable="COST 0.5 CURRENCY". ...Resultant variable="COST0.5CURRENCY". | 1
190 | 1 | 0 | GetNextEnvironment: Adaptive Comfort being reported during design day. | 1
191 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.158E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE ANN CLG 0.4% CONDNS DB=>MCWB, at Simulation time=08/21 00:00 - 00:10 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 16376.25 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 0.18970464 m3/s. ...Air Mass Flow Rate = 0.21856847 kg/s. ...Air Density = 1.15215145 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99927.000 Pa. ...Inlet Air Dry-Bulb Temp = 24.973 C. ...Inlet Air Humidity Ratio = 8.50181529E-003 kgWater/kgDryAir. | 0
192 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.826E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE ANN CLG 0.4% CONDNS DB=>MCWB, at Simulation time=08/21 00:00 - 00:10 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 67716.92 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 1.23631139 m3/s. ...Air Mass Flow Rate = 1.42461810 kg/s. ...Air Density = 1.15231333 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99927.000 Pa. ...Inlet Air Dry-Bulb Temp = 25.045 C. ...Inlet Air Humidity Ratio = 8.26065121E-003 kgWater/kgDryAir. | 0
193 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.826E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE ANN CLG 0.4% CONDNS DB=>MCWB, at Simulation time=08/21 00:00 - 00:10 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 67716.92 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 1.23631139 m3/s. ...Air Mass Flow Rate = 1.42461810 kg/s. ...Air Density = 1.15231333 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99927.000 Pa. ...Inlet Air Dry-Bulb Temp = 25.045 C. ...Inlet Air Humidity Ratio = 8.26065121E-003 kgWater/kgDryAir. | 0
194 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 1.02 C. ...Occurrence info = SAN-DIEGO-GILLESPIE ANN CLG 0.4% CONDNS DB=>MCWB, 08/21 05:40 - 05:50 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 24.467 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
195 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 1.98 C. ...Occurrence info = SAN-DIEGO-GILLESPIE ANN CLG 0.4% CONDNS DB=>MCWB, 08/21 15:40 - 15:45 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 28.099 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
196 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 1-2" did not converge after 25 warmup days. See Warmup Convergence Information in .eio file for details. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 1.33E-002 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 4.60E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 7.8574E-003 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 8.5651E-002 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
197 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 1-4" did not converge after 25 warmup days. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 3.86E-002 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 3.77E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 5.6954E-003 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 4.0910E-002 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
198 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 1-9" did not converge after 25 warmup days. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 5.05E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 3.27E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 1.8962E-003 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 0.1329 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
199 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 1-1" did not converge after 25 warmup days. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 1.96E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 5.55E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 1.0015E-003 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 0.6426 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
200 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 2-7" did not converge after 25 warmup days. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 6.91E-002 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 1.75E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 5.1004E-004 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 0.2957 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
201 | 1 | 1 | CheckWarmupConvergence: Loads Initialization, Zone="THERMAL ZONE 2-12" did not converge after 25 warmup days. ...Environment(RunPeriod)="SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907" ..Max Temp Comparison = 8.39E-004 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Min Temp Comparison = 2.13E-003 vs Temperature Convergence Tolerance=0.40 - Pass Convergence ..Max Heat Load Comparison = 3.2611E-004 vs Loads Convergence Tolerance=4.00E-002 - Pass Convergence ..Max Cool Load Comparison = 0.1459 vs Loads Convergence Tolerance=4.00E-002 - Fail Convergence | 1
202 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-24¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 08:35 - 08:40 | 0
203 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-13¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 08:40 - 08:50 | 0
204 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-13¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 08:40 - 08:50 | 0
205 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-12¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:00 - 09:10 | 0
206 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-22¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:00 - 09:10 | 0
207 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-14¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:30 - 09:40 | 0
208 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-23¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:35 - 09:38 | 0
209 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-21¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:40 - 09:50 | 0
210 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-17¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:48 - 09:50 | 0
211 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-15¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:50 - 10:00 | 0
212 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-16¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 09:58 - 10:00 | 0
213 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-7¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:00 - 10:10 | 0
214 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-17¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:00 - 10:10 | 0
215 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-6¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:00 - 10:10 | 0
216 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-14¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:00 - 10:10 | 0
217 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-18¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:05 - 10:08 | 0
218 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-11¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:05 - 10:08 | 0
219 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-12¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:23 - 10:27 | 0
220 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-15¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:23 - 10:27 | 0
221 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-21¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:30 - 10:40 | 0
222 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-3¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:40 - 10:50 | 0
223 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-20¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:40 - 10:50 | 0
224 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-23¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 10:40 - 10:50 | 0
225 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-3¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:00 - 11:10 | 0
226 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-7¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:00 - 11:10 | 0
227 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-8¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:00 - 11:10 | 0
228 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-6¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:10 - 11:20 | 0
229 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-25¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:10 - 11:20 | 0
230 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-5¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 11:50 - 12:00 | 0
231 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-9¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 13:00 - 13:10 | 0
232 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-22¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 13:00 - 13:10 | 0
233 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-11¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 13:30 - 13:40 | 0
234 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-10¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 14:10 - 14:20 | 0
235 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-8¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 14:10 - 14:20 | 0
236 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-4¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 14:30 - 14:40 | 0
237 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-2¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 15:10 - 15:20 | 0
238 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 16:35 - 16:40 | 0
239 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-9¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 16:40 - 16:50 | 0
240 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 16:40 - 16:45 | 0
241 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/01 17:40 - 17:50 | 0
242 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-20¦VTU-1" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/08 16:40 - 16:50 | 0
243 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 4¦VRF-1". ...InitVRF: VRF Heat Pump Min/Max Operating Temperature in Cooling Mode Limits have been exceeded and VRF system is disabled. ... Outdoor Unit Inlet Air Temperature = -6.000 ... Cooling Minimum Outdoor Unit Inlet Temperature = -5.000 ... Cooling Maximum Outdoor Unit Inlet Temperature = 43.000 ... Check VRF Heat Pump Min/Max Outdoor Temperature in Cooling Mode limits. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/11 23:40 - 23:50 | 0
244 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 1¦VRF-1". ...InitVRF: VRF Heat Pump Min/Max Operating Temperature in Heating Mode Limits have been exceeded and VRF system is disabled. ... Outdoor Unit Inlet Air Temperature = -20.100 ... Heating Minimum Outdoor Unit Inlet Temperature = -20.000 ... Heating Maximum Outdoor Unit Inlet Temperature = 20.000 ... Check VRF Heat Pump Min/Max Outdoor Temperature in Heating Mode limits. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/12 01:50 - 02:00 | 0
245 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 4¦VRF-1". ...InitVRF: VRF Heat Pump Min/Max Operating Temperature in Heating Mode Limits have been exceeded and VRF system is disabled. ... Outdoor Unit Inlet Air Temperature = -23.600 ... Heating Minimum Outdoor Unit Inlet Temperature = -20.000 ... Heating Maximum Outdoor Unit Inlet Temperature = 20.000 ... Check VRF Heat Pump Min/Max Outdoor Temperature in Heating Mode limits. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=01/12 02:50 - 02:55 | 0
246 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.785E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=03/18 00:00 - 00:01 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 67716.92 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 1.20853720 m3/s. ...Air Mass Flow Rate = 1.42461810 kg/s. ...Air Density = 1.17879540 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99883.333 Pa. ...Inlet Air Dry-Bulb Temp = 19.362 C. ...Inlet Air Humidity Ratio = 5.79621068E-003 kgWater/kgDryAir. | 0
247 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.097E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=03/18 00:00 - 00:01 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 67716.92 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 0.74266697 m3/s. ...Air Mass Flow Rate = 0.88329082 kg/s. ...Air Density = 1.18934982 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99883.333 Pa. ...Inlet Air Dry-Bulb Temp = 16.763 C. ...Inlet Air Humidity Ratio = 5.80465466E-003 kgWater/kgDryAir. | 0
248 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range at 1.097E-005 m3/s/W. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=03/18 00:00 - 00:01 ...Expected range for VolumeFlowPerRatedTotalCapacity=[2.684E-005--6.713E-005] ...Possible causes include inconsistent air flow rates in system components, ...or mixing manual inputs with autosize inputs. Also check the following values and calculations. ...Volume Flow Rate per Rated Total Capacity = Volume Flow Rate / Rated Total Capacity ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Data used for calculations: ...Rated Total Capacity = 67716.92 W. ...Volume Flow Rate = Air Mass Flow Rate / Air Density ...Volume Flow Rate = 0.74266697 m3/s. ...Air Mass Flow Rate = 0.88329082 kg/s. ...Air Density = 1.18934982 kg/m3. ...Data used for air density calculation: ...Outdoor Air Pressure = 99883.333 Pa. ...Inlet Air Dry-Bulb Temp = 16.763 C. ...Inlet Air Humidity Ratio = 5.80465466E-003 kgWater/kgDryAir. | 0
249 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -10.97 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 19.362 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
250 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -10.97 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 19.362 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
251 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -34.17 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 16.762 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
252 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -34.17 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 16.762 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
253 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-7¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.37 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
254 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-12¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 0.56 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
255 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-14¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.28 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
256 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-15¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.75 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
257 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-16¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.96 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
258 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-17¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.95 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
259 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-20¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.65 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
260 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-21¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.70 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
261 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-22¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.21 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
262 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-23¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 0.57 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 03/18 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 10.127 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
263 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=03/18 00:01 - 00:02 | 0
264 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-7¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 0.84 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/25 00:00 - 00:02 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 14.590 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
265 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-13¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 1.00 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/25 00:00 - 00:02 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 14.590 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
266 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-9¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.10 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
267 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-10¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.37 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
268 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-11¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -0.46 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
269 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-20¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -2.71E-002 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
270 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-8¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 1.99E-002 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
271 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-12¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -1.43 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 14.911 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
272 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-21¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = 0.32 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
273 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-22¦VTU-1¦VRF COOLING COIL" - Full load outlet air dry-bulb temperature < 2C. This indicates the possibility of coil frost/freeze. Outlet temperature = -9.38E-002 C. ...Occurrence info = SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, 04/29 00:00 - 00:01 ... Possible reasons for low outlet air dry-bulb temperatures are: This DX coil 1) may have a low inlet air dry-bulb temperature. Inlet air temperature = 12.856 C. 2) may have a low air flow rate per watt of cooling capacity. Check inputs. 3) is used as part of a HX assisted cooling coil which uses a high sensible effectiveness. Check inputs. | 0
274 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=05/27 00:01 - 00:03 | 0
275 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5" Terminal unit part-load ratio calculation failed: PLR limits of 0 to 1 exceeded Please fill out a bug report and forward to the EnergyPlus support group. Environment=SAN-DIEGO-GILLESPIE - USA Custom-722907 WMO#=722907, at Simulation time=07/15 00:03 - 00:04 | 0
276 | 1 | 0 | The following Report Variables were requested but not generated because IDF did not contain these elements or misspelled variable name -- check .rdd file | 1
277 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 58236
278 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 35456
279 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 558
280 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 454
281 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 304
282 | 1 | 0 | Coil:Heating:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF HEATING COIL" - Air volume flow rate per watt of rated total heating capacity is out of range error continues... | 264
283 | 1 | 0 | Temperature out of range [-100. to 200.] (PsyPsatFnTemp) | 2450
284 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 3952253
285 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 7208175
286 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 5379694
287 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 36291
288 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 7918
289 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-24¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 5867
290 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-13¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 20538
291 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-13¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 14676
292 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-12¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 19391
293 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-22¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 23832
294 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-14¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 11874
295 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-23¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 23452
296 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-21¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 20646
297 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-17¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 34225
298 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-15¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 9575
299 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-16¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 33858
300 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-7¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 20253
301 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-17¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 20632
302 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-6¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 21219
303 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-14¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 33329
304 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-18¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 8245
305 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-11¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 5569
306 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-12¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 31053
307 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-15¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 33372
308 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-21¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 33285
309 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-3¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 23287
310 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-20¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 33462
311 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-23¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 32045
312 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-3¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 11889
313 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-7¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 32486
314 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-8¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 17534
315 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-6¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 12660
316 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-25¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 26060
317 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-5¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 16662
318 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-9¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 15190
319 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-22¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 31792
320 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-11¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 15266
321 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-10¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 13806
322 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-8¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 13589
323 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-4¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 9570
324 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-2¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 8005
325 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 30897
326 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 2-9¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 10713
327 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 13495
328 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-26¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 6156
329 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-20¦VTU-1" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 11098
330 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 4¦VRF-1" -- Exceeded VRF Heat Pump min/max cooling temperature limit error continues... | 116
331 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 1¦VRF-1" -- Exceeded VRF Heat Pump min/max heating temperature limit error continues... | 88
332 | 1 | 0 | AirConditioner:VariableRefrigerantFlow "VRF LOOP 4¦VRF-1" -- Exceeded VRF Heat Pump min/max heating temperature limit error continues... | 43
333 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 1028
334 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 540
335 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF COOLING COIL" - Air volume flow rate per watt of rated total cooling capacity is out of range error continues... | 497
336 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-2¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 65
337 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 52
338 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 50
339 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 47
340 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-7¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 12
341 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-12¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 9
342 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-14¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 17
343 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-15¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 28
344 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-16¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 32
345 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-17¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 32
346 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-20¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 24
347 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-21¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 27
348 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-22¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 11
349 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 2-23¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 10
350 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-3" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 5
351 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-7¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 91
352 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-13¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 96
353 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-9¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 8
354 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-10¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 12
355 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-11¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 15
356 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-20¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 4
357 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-8¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 7
358 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-12¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 68
359 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-21¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 13
360 | 1 | 0 | Coil:Cooling:DX:VariableRefrigerantFlow "THERMAL ZONE 1-22¦VTU-1¦VRF COOLING COIL" - Full load outlet temperature indicates a possibility of frost/freeze error continues. Outlet air temperature statistics follow: | 7
361 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-4" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 3
362 | 1 | 0 | ZoneHVAC:TerminalUnit:VariableRefrigerantFlow "THERMAL ZONE 1-1¦VTU-5" -- Terminal unit part-load ratio limits of 0 to 1 exceeded error continues... | 2